## MASS BALNC
CHAPTER 2 : MASS BALANCE CALCULATION
ITERATION : 1
Assumptions:
(a) 82 MLD flow to PST followed by SBR
(b) 18 MLD flow shall be directly fed to SBR
2.1 | PRIMARY SLUDGE GENERATED (FROM PST)
- | Inlet sewage flow to Primary Clarifier
| Flow | : | 82 | MLD
| TSS | : | 400 | mg/L : | 32800 | kg/day
| BOD5 | : | 350 | mg/L : | 28700 | kg/day
| TP | : | 7 | mg/L : | 574 | kg/day
| Org-N | : | 10 | mg/L : | 820 | kg/day
| NH3-N | : | 50 | mg/L : | 4100 | kg/day
| TKN | : | 60 | mg/L : | 4920 | kg/day
| VSS | : | 280 | mg/L : | 22960 | kg/day
| Organic fraction (TVSS/TSS) | : | 280 mg/L/400 mg/L
|  | : | 0.7
- | Sludge generated from Primary Clarifier
Assume 60% TSS removal
| TSS in sludge | : | % removal * Inlet TSS
|  | : | 0.6*32800 kgSS/day
|  | : | 19680 | kg/day
| Specific gravity of sludge | : | 1.03
| Consistency of sludge | : | 4 | %
| Primary sludge flow | : | 477.6699 | m3/d
Assume 35% BOD5 removal
| BOD5 in sludge | : | % removal * Inlet BOD5
|  | : | 0.35*28700 kg BOD5/day
|  | : | 10045 | kg/day
Assume 10% TP removal
| TP in sludge | : | % removal * Inlet TP
|  | : | 0.10*574 kg TP/day
|  | : | 57.4 | kg/day
Assume 40% Org-N removal
| Org-N in sludge | : | % removal * Inlet Org-N
|  | : | 0.4*820 kg Org-N /day
|  | : | 328 | kg/day
NH3-N removal is assumed to be zero
| NH3-N in sludge | : | 0 | kg/day
| TKN in sludge | : | Org-N in sludge + NH3-N in sludge
|  | : | 328 | kg/day
| Organic fraction in primary sludge (TVSS/TSS) | : | 0.7
2.2 | SECONDARY SLUDGE GENERATED FROM SBR
* Refer Annexure -III for sludge production calculation
| Excess sludge (WAS) produced* | : | 13300 | kg/day
| Specific gravity of WAS | : | 1.02
| Consistency of WAS | : | 0.8 | %
| Excess sludge flow | : | 1629.902 | m3/day
| Soluble BOD5 in the effluent (S) | : | Total BOD5 in the Effluent - BOD5 exerted by TSS in the effluent
| BOD5 exerted by TSS in effluent | : | (10 mg/L TSS) x (0.65 biodegradable solids/kg TSS) x (1.42 kg BODL/ kg biodegradable solids) x (0.68 kg BOD5 / kg BODL)
|  | : | 6.2764 | mg/L
| Soluble BOD5 in the effluent (S) | : | (10-6.28) | mg/L
|  | : | 3.7236 | mg/L
| Soluble BOD5 | : | 6.0691 | kg/day
| BOD5 exerted by TSS in the sludge | : | (TSS in sludge in kg/day) x (0.65 biodegradable solids/kg TSS) x (1.42 kg BODL/ kg biodegradable solids) x (0.68 kg BOD5 / kg BODL)
|  | : | 8347.612 | kg/day
| Total BOD5 in the sludge from SBR | : | BOD5 exerted by TSS + Soluble BOD5 in sludge
|  | : | (8347 +6.07) kg/day
|  | : | 8353.6811 | kg/day
| TP* | : | 549 | kg/day
| Org-N in TSS * | : | 1058 | kg/day
| NH3- N * | : | 1.6 | kg/day
| TKN* | : | 1059.6 | kg/day
| Nitrate -N* | : | 11.4 | kg/day
| TN* | : | 1071 | kg/day
| Organic fraction in secondary sludge sludge (TVSS/TSS)* | : | 0.7
2.3 | MECHANICAL SCREW THICKENER
- | Inlet Sludge flow
| TSS | : | TSS in (Primary sludge + SBR sludge)
|  | : | 19680 kg/day + 13300 kg/day
|  | : | 32980 | kg/day
| Specific gravity of combined sludge | : | 1.025
| Consistency of combined sludge | : | ((32980)/(1.025*(1629.9 + 477.67))/10
|  | : | 1.5267 | %
| Combined sludge flow | : | 2107.5719 | m3/d
| Poly dosing considered for design purpose | : | 2 | kg/MT of inlet TSS
| TSS generated due to polyelectrolyte | : | 2 kg*32.980 MT/day
|  | : | 65.96 | kg/day
| Total inlet TSS | : | 32980 kg/day + 65.96 kg/day
|  | : | 33045.96 | kg/day
| BOD5 | : | BOD5 in (Primary sludge + SBR sludge)
|  | : | 10045 kg/day + 8353.68 kg/day
|  | : | 18398.6811 | kg/day
| TP | : | TP in (Primary sludge + SBR sludge)
|  | : | 57.4 kg/day + 549 kg/day
|  | : | 606.4 | kg/day
| Org-N | : | Org-N in (Primary sludge + SBR sludge)
|  | : | 328 kg/day + 1058 kg/day
|  | : | 1386 | kg/day
| NH3- N | : | NH3-N in (Primary sludge + SBR sludge)
|  | : | 0 kg/day +1.6 kg/day
|  | : | 1.6 | kg/day
| TKN | : | Org-N in sludge + NH3-N in sludge
|  | : | 1386 kg/day + 1.6 kg/day
|  | : | 1387.6 | kg/day
| Organic fraction in inlet sludge (TVSS/TSS) | : | (Organic fraction of solids in the inlet solids)/Total inlet solids
|  | : | ((0.7 * 19680 kg/day) + (0.7 * 13300 kg/day)) / 32980kg/day
|  | : | 0.7 | (Effect of sludge due to polelectrolyte is insignificant)
- | Thickened sludge underflow
| Solids capture rate for (PST +SBR) sludge | : | 95%
| Solids capture rate for sludge generated by polyelectrolyte | : | 80%
| TSS in the thickened Sludge | : | Solids capture rate * inlet TSS
| Total TSS | : | 0.95*32980 kg/day + 0.8*65.96 kg/day
|  | : | 31383.768 | kg/day
| Specific gravity of sludge | : | 1.03
| Consistency of sludge | : | 8 | %
| Thickened sludge flow | : | 380.871 | m3/d
| BOD5 | : | Solids capture rate * inlet BOD5
|  | : | 0.95*18398.68 kg/day
|  | : | 17478.747 | kg/day
| TP | : | Solids capture rate * inlet TP
|  | : | 0.95*606.40 kg/day
|  | : | 576.08 | kg/day
| Org-N | : | Solids capture rate* inlet Org-N
|  | : | 0.95*1386 kg/day
|  | : | 1316.7 | kg/day
| NH3-N | : | Inlet NH3-N *(Sludge underflow/ thickener inlet flow)
|  | : | 1.6 kg/day*(380.87 m3/day/2107.57 m3/day)
|  | : | 0.28914 | kg/day
| TKN | : | Org-N in sludge + NH3-N in sludge
|  | : | 1316.70 kg/day + 0.29 kg/day
|  | : | 1316.9891 | kg/day
| Organic fraction (TVSS/TSS) | : | 0.7
- | Filtrate flow
| Filtrate flow | : | 2107.57 m3/day - 380.87 m3/day
|  | : | 1726.7009 | m3/d
| TSS | : | Inlet TSS - TSS in Thickened Sludge
|  | : | 33045.96 kg/day - 31383.77 kg/day
|  | : | 1662.192 | kg/day
| BOD5 | : | Inlet BOD5 - BOD5 in Thickened Sludge
|  | : | 18398.68 kg/day - 17478.75 kg/day
|  | : | 919.9341 | kg/day
| TP | : | Inlet TP - TP in Thickened Sludge
|  | : | 606.40 kg/day - 576.08 kg/day
|  | : | 30.32 | kg/day
| Org-N | : | Inlet Org-N - Org-N in Thickened Sludge
|  | : | 1386 kg/day - 1316.7 kg/day
|  | : | 69.3 | kg/day
| NH3-N | : | Inlet NH3-N - NH3-N in Thickened Sludge
|  | : | 1.6 kg/day - 0.29 kg/day
|  | : | 1.3109 | kg/day
| TKN | : | (NH3-N + Org-N) in filtrate
|  | : | 69.3 kg/day + 1.31 kg/day
|  | : | 70.6109 | kg/day
2.4 | SLUDGE FROM EXISTING 60 MLD STP
- | Inlet sewage flow to Primary clarifier
| Flow | : | 60 | MLD
| TSS | : | 400 | mg/L : | 24000 | kg/day
| BOD5 | : | 350 | mg/L : | 21000 | kg/day
| TP | : | 7 | mg/L : | 420 | kg/day
| Org-N | : | 10 | mg/L : | 600 | kg/day
| NH3-N | : | 50 | mg/L : | 3000 | kg/day
| TKN | : | 60 | mg/L : | 3600 | kg/day
| VSS | : | 280 | mg/L
| Organic fraction (TVSS/TSS) | : | 280 mg/L/400 mg/L
|  | : | 0.7
- | Primary sludge produced
Assume 60% TSS removal
| TSS in sludge | : | % removal * Inlet TSS
|  | : | 0.6*24000 kg/day
|  | : | 14400 | kg/day
| Specific gravity of sludge | : | 1.03
| Consistency of sludge | : | 4 | %
| Primary sludge flow | : | 349.5146 | m3/d
Assume 35% BOD5 removal
| BOD5 in sludge | : | % removal * Inlet BOD5
|  | : | 0.35*21000 kg/day
|  | : | 7350 | kg/day
Assume 10% TP removal
| TP in sludge | : | % removal * Inlet TP
|  | : | 0.10*420 kg/day
|  | : | 42 | kg/day
Assume 40% Org-N removal
| Org-N in sludge | : | % removal * Inlet Org-N
|  | : | 0.4*600 kg/day
|  | : | 240 | kg/day
NH3-N removal is assumed to be zero
| NH3-N in sludge | : | 0 | kg/day
| TKN in sludge | : | Org-N in sludge + NH3-N in sludge
|  | : | 240 kg/day + 0 kg/day
|  | : | 240 | kg/day
| Organic fraction (TVSS/TSS) | : | 0.7
- | Secondary sludge produced
| BOD5 removed in Primary clarifier | : | 35 | %
|  | : | 0.35*350 mg/L
|  | : | 122.5 | mg/L
| BOD5 influent to Aeration tank | : | 227.5 | mg/L
| Required BOD5 at the outlet | : | 10 | mg/L
| Kg of BOD5 removed in aeration tank | : | (227.5 mg/L – 10 mg/L) x 60 MLD
|  | : | 13050 | kg/day
NOTE: Sludge production in extended aeration process is less than 0.45 kgTSS/kg BOD removed. However, sludge yield is assumed as 0.5 kg TSS/kg BOD removed, in case of non - availability of parameters for existing STP for safer side.
| Sludge production (TSS) | : | 0.5 kg TSS / kg BOD5 removed
|  | : | 0.5*13050 kg/day
|  | : | 6525 | kg/day
| Specific gravity of sludge | : | 1.02
| Consistency of sludge | : | 0.8 | %
| Secondary sludge flow | : | 799.6324 | m3/d
| BOD5 in the secondary sludge | : | (TSS in sludge in kg/day) x (0.65 biodegradable solids/kg TSS) x (1.42 kg BODL/ kg biodegradable solids) x (0.68 kg BOD5 / kg BODL)
|  | : | 6525 kg/day *0.65 *1.42 *0.68
|  | : | 4095.351 | kg/day
| Soluble BOD5 in the effluent (S) | : | Total BOD5 in the Effluent - BOD5 exerted by TSS in the effluent
| BOD5 exerted by TSS in effluent | : | (Required outlet TSS) x (0.65 biodegradable solids/kg TSS) x (1.42 kg BODL/ kg biodegradable solids) x (0.68 kg BOD5 / kg BODL)
|  | : | 6.2764 | mg/L
| Soluble BOD5 in the sludge (mg/L) | : | 10 mg/L - 6.3 mg/L
|  | : | 3.7236 | mg/L
| Soluble BOD5 in the sludge (kg/day) | : | 3.7 mg/L*Sludge flow
| Sludge flow | : | 799.6324 | m3/d
| Soluble BOD5 in the sludge | : | 3.7 mg/L*0.799 MLD
|  | : | 2.9775 | kg/day
| Total BOD5 in Secondary sludge | : | BOD5 exerted by TSS + Soluble BOD5 in the sludge
|  | : | 4095.35 kg/day + 2.98 kg/day
|  | : | 4098.3285 | kg/day
| Org-N in TSS (Soluble org-N is neglected, since small quantity) | : | 0.122 kg org-N/kg TVSS x 0.8 kg TVSS/kg TSS
|  | : | 0.122*0.8*6525 kg/day
|  | : | 636.84 | kg/day
| NH3-N | : | 1 | g/m3 of sludge
|  | : | 0.79963 | kg/day
| TP removed in primary clarifier | : | 10 | %
|  | : | 0.1*7 mg/L
|  | : | 0.7 | mg/L
| TP in the influent to aeration tank | : | 6.3 | mg/L
| TP required in the final treated effluent | : | 1 | mg/L
| TP in secondary sludge | : | (6.3 mg/L – 1 mg/L) x 60 MLD
|  | : | 318 | kg/day
| Organic fraction (TVSS/TSS) | : | 0.8
- | SCREW THICKENER FOR THICKENING OF SLUDGE FROM EXISTING STP
- | Inlet Sludge flow
| TSS | : | TSS in (Primary sludge + Secondary sludge)
|  | : | 14400 kg/day + 6525 kg/day
|  | : | 20925 | kg/day
| Specific gravity of sludge | : | 1.025
| Consistency of combined sludge | : | ((20925)/(1.025*(799.63 + 349.51))/10
|  | : | 1.7765 | %
| Inlet sludge flow | : | 1149.1469 | m3/d
| Poly dosing considered for design purpose | : | 2 | kg/MT of inlet TSS
| TSS generated due to polyelectrolyte | : | 2 kg*20.925 MT/day
|  | : | 41.85 | kg/day
| Total inlet TSS | : | 20925 kg/day + 41.85 kg/day
|  | : | 20966.85 | kg/day
| BOD5 | : | BOD5 in (Primary sludge + Secondary sludge)
|  | : | 7350 kg/day + 4098.3 kg/day
|  | : | 11448.3285 | kg/day
| TP | : | TP in (Primary sludge + Secondary sludge)
|  | : | 42 kg/day + 318 kg/day
|  | : | 360 | kg/day
| Org-N | : | Org-N in (Primary sludge + Secondary sludge)
|  | : | 240 kg/day + 636.84 kg/day
|  | : | 876.84 | kg/day
| NH3-N | : | NH3-N in (Primary sludge + Secondary sludge)
|  | : | 0 kg/day + 0.8 kg/day
|  | : | 0.79963 | kg/day
| TKN | : | Org-N in inlet sludge + NH3-N in inlet sludge)
|  | : | 876.84 kg/day + 0.8 kg/day
|  | : | 877.6396 | kg/day
| Organic fraction in inlet sludge (TVSS/TSS) | : | ((Organic fraction of solids in the inlet solids)/Total inlet solids
|  | : | ((0.7*14400 kg/day)+(0.8*6525 kg/day))/20925 kg/day
|  | : | 0.73118
- | Thickened sludge underflow
| Solids capture rate for sludge | : | 95%
| Solids capture rate for sludge generated by polyelectrolyte | : | 80%
| TSS in the thickened Sludge | : | Solids capture rate * inlet TSS
| Total TSS | : | 0.95*20925 kg/day + 0.8*41.85 kg/day
|  | : | 19912.23 | kg/day
| Specific gravity of sludge | : | 1.03
| Consistency of sludge | : | 8 | %
| Thickened sludge flow | : | 241.6533 | m3/d
| BOD5 | : | Solids capture * Inlet BOD5
|  | : | 0.95*11448.33 kg/day
|  | : | 10875.9121 | kg/day
| TP | : | Solids capture * Inlet TP
|  | : | 0.95*360 kg/day
|  | : | 342 | kg/day
| Org-N | : | Solids capture * Inlet Org-N
|  | : | 0.95*876.84 kg/day
|  | : | 832.998 | kg/day
| NH3-N | : | Inlet NH3-Nx(thickener underflow/thickener inlet flow)
|  | : | 0.8*(241.86 m3day/1149.15 m3/day)
|  | : | 0.16815 | kg/day
| TKN | : | Org-N in the sludge + NH3-N in the sludge
|  | : | 833 kg/day + 0.17 kg/day
|  | : | 833.1662 | kg/day
| Organic fraction (TVSS/TSS) | : | 0.73118
2.5 | ANAEROBIC DIGESTER
- | Inlet thickened sludge flow
| Sludge flow/mass | : | Thickened sludge from proposed STP + Thickened sludge from existing plant
| TSS | : | 31383.77 kg/day + 19912.23 kg/day
|  | : | 51295.998 | kg/day
| Specific gravity of sludge | : | 1.03
| Consistency of sludge | : | ((51296)/(1.03*(380.87+241.65))/10
|  | : | 8 | %
| Sludge flow (Vinfluent) | : | 622.5242 | m3/d
| BOD5 | : | 17478.75 kg/day + 10875.91 kg/day
|  | : | 28354.6591 | kg/day
| TP | : | 576.08 kg/day + 342 kg/day
|  | : | 918.08 | kg/day
| Org-N | : | 1316.70 kg/day + 833 kg/day
|  | : | 2149.698 | kg/day
| NH3-N | : | 0.29 kg/day + 0.17 kg/day
|  | : | 0.4573 | kg/day
| TKN | : | 2149.70 kg/day + 0.46 kg/day
|  | : | 2150.1553 | kg/day
| Inlet organic Fraction | : | (Organic fraction of solids in thickened sludge from proposed STP + organic fraction of solids in thickened sludge from existing STP)/Total solids in the thickened sludge)
|  | : | ((0.73*19912.23 kg/day) + (0.7*31383.77 kg/day)) / 51296 kg/day
|  | : | 0.7121
| Inlet TVSS | : | 71.2105 | % of TSS
|  | : | 0.71*51296 kg/day
|  | : | 36528.1176 | kg/day
- | Digested Sludge flow
Basic assumptions
| BOD5 Stabilisation | : | 60 | %
| Percentage of VSS destructed | : | (0.67*T + 36 )/100 (Ref.: 9)
|  | : | (0.67*24oC+36)/100
|  | : | 52.08 | %
| Conversion of Org-N into NH3-N | : | 15 | %
| Conversion of Org-N to soluble Org-N | : | 10 | %
| TSS remaining in digested sludge (Wremaining) | : | VSS remaining after stabilisation + Inert solids
|  | : | 0.71 x 0.48 x Inlet TSS + (1-0.71) x Inlet TSS
|  | : | 32272.1544 | kg/day
| TVSS remaining in the digested sludge | : | 47.92 | % of inlet TVSS
|  | : | 17504.274 | kg/day
NOTE: Anaerobic digestion in the proposed STP is considered as a high rate digestion process with continuous complete mixed system and therefore, no supernatant flow to be generated. Moreover, it is also assumed that no liquid volume change occurs in the digetser. Hence, Inlet thickened Sludge flow,Vinfluent = Digested Sludge flow,Vsludge.
| Total digested sludge, Wsludge = Wremaining | : | 32272.1544 | kg/day
| Organic fraction in digested sludge (TVSS/TSS) | : | 17504.27 kg/day /32272.15 kg/day
|  | : | 0.5424
| TSS remaining in digested,sludge (Wremaining) | : | TSS in digested sludge removed from digester(Wsludge)
| Vsludge | : | Wsludge/(Consistency*1.03*1000 kg/m3)………..…(a)
| Wsludge | : | 32272.1544 | kg/day
| Vsludge = Vinfluent | : | 622.5242 | m3/d
By substituting the value of Wsludge and Vsludge in equation (a), we get
| Consistency of digested sludge | : | 32272.15 kg/day/(1.03*1000 kg/m3*622.52 m3/d)
|  | : | 0.050331
|  | : | 5.0331 | %
| BOD5 in digested sludge | : | Unstabilised BOD5
| Unstabilised BOD5 | : | (1 - 0.6 Stabilised) * Inlet BOD5 to digester
|  | : | 11341.8637 | kg/day
| BOD5 in digested sludge | : | 11341.8637 | kg/day
| TP in the digested sludge | : | Inlet TP
|  | : | 918.08 | kg/day
| Org-N in digested sludge | : | Inlet Org-N x (1- 0.15 (converted into NH3-N))
|  | : | 2149.7 kg/day *(1- 0.15)
|  | : | 1827.2433 | kg/day
| NH3-N in digested sludge | : | ((Inlet Org-N x 0.15) + Inlet NH3-N)
|  | : | 0.15*2149.7 kg/day + 0.46 kg/day
|  | : | 322.912 | kg/day
| TKN in digested sludge | : | 1827.24kg/day + 322.91 kg/day
|  | : | 2150.1553 | kg/day
| Organic fraction (TVSS/TSS) | : | 0.5424
2.6 | COMBINED THICKENING AND DEWATERING MACHINE (COTDM)
- | Inlet sludge flow from digester
| TSS in the digested sludge | : | 32272.1544 | kg/day
|  | : | 622.5242 | m3/d
| Poly dosing required | : | 4 | kg/MT of inlet TSS
| Considering safety factor | : | 1.5
| Poly dosing considered for design purpose | : | 6 | kg/MT of inlet TSS
| TSS generated due to polyelectrolyte | : | 6 kg*32.272 MT/day
|  | : | 193.6329 | kg/day
| Total inlet TSS | : | 32272.15 kg/day + 193.63 kg/day
|  | : | 32465.7873 | kg/day
| BOD5 | : | 11341.8637 | kg/day
| TP | : | 918.08 | kg/day
| Org-N | : | 1827.2433 | kg/day
| NH3-N | : | 322.912 | kg/day
| TKN | : | 2150.1553 | kg/day
| Organic fraction(TVSS/TSS) | : | 0.5424 | (Effect of sludge due to polelectrolyte is insignificant)
- | Dewatered sludge characteristics
| Solids capture rate for sludge | : | 95%
| Solids capture rate for polyelectrolyte | : | 80%
| Total TSS in the dewatered sludge | : | 0.95*32272.15 kg/day + 0.8*193.63 kg/day
|  | : | 30813.453 | kg/day
| Specific gravity of sludge | : | 1.06
| Consistency of sludge | : | 25 | %
| Dewatered sludge flow | : | 116.2772 | m3/d
| BOD5 | : | Solids capture * Inlet BOD5
|  | : | 0.95*11341.86 kg/day
|  | : | 10774.7705 | kg/day
| TP | : | Solids capture * Inlet TP
|  | : | 0.95*918.08 kg/day
|  | : | 872.176 | kg/day
| Org-N | : | Solids capture * Inlet Org-N
|  | : | 0.95*1827.24 kg/day
|  | : | 1735.8811 | kg/day
| NH3-N | : | Inlet NH3-N * (Outlet flow/Inlet flow)
|  | : | 322.91 kg/day *(116.28 m3/day/622.52 m3/day)
|  | : | 60.3146 | kg/day
| TKN | : | Org-N in the sludge + NH3 -N in the sludge
|  | : | 1735.88 kg/day + 60.31 kg/day
|  | : | 1796.1957 | kg/day
| Organic fraction (TVSS/TSS) | : | 0.5424
- | Beltwash water quality
| Volume of beltwash water | : | 13.6 | L/kg TSS feed
|  | : | 13.6 * 32272.15 kg/day
|  | : | 438901.2992 | L/day
|  | : | 438.9013 | m3/d
| Say, | : | 440 | m3/d
|  | : | 0.44 | MLD
| TSS in the final treated water | : | 10 | mg/L
| TSS in the beltwash water | : | 0.44 MLD * 10 mg/L
|  | : | 4.4 | kg/day
| BOD5 in the final treated water | : | 10 | mg/L
| BOD5 in the beltwash water | : | 0.44 MLD * 10 mg/L
|  | : | 4.4 | kg/day
| TP in the final treated water | : | 1 | mg/L
| TP in the beltwash water | : | 0.44 MLD * 1mg/L
|  | : | 0.44 | kg/day
| Org-N in the final treated water | : | 2 | mg/L
| Org-N in the beltwash water | : | 0.44 MLD * 2 mg/L
|  | : | 0.88 | kg/day
| NH3-N in the final treated water | : | 1 | mg/L
| NH3-N in the beltwash water | : | 0.44 MLD * 1 mg/L
|  | : | 0.44 | kg/day
| TKN | : | Org-N in beltwash water + NH3-N in beltwash water
|  | : | 1.32 | kg/day
- | Filtrate flow from COTDM
| Flow/mass | : | Digested sludge + beltwash water - sludge cake
| Filtrate flow | : | 622.52 m3/day + 440 m3/day - 116.28 m3/day
|  | : | 946.2471 | m3/d
| TSS | : | 32465.79 kg/day + 4.40 kg/day - 30813.45 kg/day
|  | : | 1656.7343 | kg/day
| BOD5 | : | 11341.86 kg/day + 4.40 kg/day - 10774.77 kg/day
|  | : | 571.4932 | kg/day
| TP | : | 918.08 kg/day + 0.44 kg/day - 872.18 kg/day
|  | : | 46.344 | kg/day
| Org-N | : | 1827.24 kg/day + 0.88 kg/day - 1735.88 kg/day
|  | : | 92.2422 | kg/day
| NH3-N | : | 322.91 kg/day + 0.44 kg/day - 60.31 kg/day
|  | : | 263.0374 | kg/day
| TKN | : | Org-N in the filtrate + NH3-N in the filtrate
|  | : | 92.24 kg/day +263.04 kg/day
|  | : | 355.2796 | kg/day
2.7 | BACKWASH WATER FROM DISC FILTER
| Inlet flow to Disc filter | : | 68 | MLD
| Backwash water | : | 2 % of 68 MLD
|  | : | 1.36 | MLD
| Outlet flow from Disc filter | : | 66.64 | MLD
:
- | TSS in the Disc filter inlet | : | 20 | mg/L (For design purpose)
| TSS in the Disc filter inlet in kg/day | : | 20 mg/L * 68 MLD
|  | : | 1360 | kg/day
| TSS in the Disc filter outlet | : | 5 | mg/L
| TSS in the Disc filter outlet in kg/day | : | 5 mg/L * 66.64 MLD
|  | : | 333.2 | kg/day
| TSS in the backwash water | : | (1360 - 333.2) kg/day
|  | : | 1026.8 | kg/day
- | BOD5 in the Disc filter inlet | : | 13 | mg/L (For design purpose)
| BOD5 in the Disc filter inlet in kg/day | : | 13 mg/L * 68 MLD
|  | : | 884 | kg/day
| BOD5 in the Disc filter outlet | : | 10 | mg/L
| BOD5 in the Disc filter outlet in kg/day | : | 10 mg/L * 66.64 MLD
|  | : | 666.4 | kg/day
| BOD5 in the backwash water | : | (884 - 666.4) kg/day
|  | : | 217.6 | kg/day
- | Very negligible TP load will be removed from the filtration unit. Hence, TP in backwash outlet flow = TP in inlet to disc filter - TP in the outlet from disc filter.
| TP in the Disc filter inlet | : | 1 | mg/L
| TP in the Disc filter inlet in kg/day | : | 1 mg/L * 68 MLD
|  | : | 68 | kg/day
| TP in the Disc filter outlet | : | 1 | mg/L
| TP in the Disc filter outlet in kg/day | : | 1 mg/L *66.64 MLD
|  | : | 66.64 | kg/day
| TP in the backwash water | : | (68 - 66.64) kg/day
|  | : | 1.36 | kg/day
- | Very negligible Org-N load will be removed from the filtration unit. Hence, Org-N in backwash outlet flow = Org-N in inlet to disc filter - Org-N in the outlet from disc filter.
| Org-N in the Disc filter inlet | : | 2 | mg/L
| Org-N in the Disc filter inlet in kg/day | : | 2 mg/L * 68 MLD
|  | : | 136 | kg/day
| Org-N in the Disc filter outlet | : | 2 | mg/L
| Org-N in the Disc filter outlet in kg/day | : | 2 mg/L * 66.64 MLD
|  | : | 133.28 | kg/day
| Org-N in the backwash water | : | (136 - 133.28) kg/day
|  | : | 2.72 | kg/day
- | Very negligible NH3-N load will be removed from the filtration unit. Hence, NH3-N in backwash outlet flow = NH3-N in inlet to disc filter - NH3-N in the outlet from disc filter.
| NH3-N in the Disc filter inlet | : | 1 | mg/L
| NH3-N in the Disc filter inlet in kg/day | : | 1 mg/L * 68 MLD
|  | : | 68 | kg/day
| NH3-N in the Disc filter outlet | : | 1 | mg/L
| NH3-N in the Disc filter outlet in kg/day | : | 1 mg/L * 66.64 MLD
|  | : | 66.64 | kg/day
| NH3-N in the backwash water | : | (68 - 66.64) kg/day
|  | : | 1.36 | kg/day
| TKN in the backwash water | : | (NH3-N + Org-N ) in backwash water
|  | : | (2.72 + 1.36) kg/day
|  | : | 4.08 | kg/day
:
2.8 | TOTAL COMBINED OTHERFLOW TO BE RECYCLED BACK TO INLET CHAMBER OF STP
| Total Filtrate composition | : | Filtrate flow from thickener + Centrate flow from COTDM + Backwash water from Filter
| Flow | : | (1726.7 + 946.25 + 1360) m3/day
|  | : | 4032.948 | m3/d, say 4100 m3/day
| TSS | : | (1662.19 + 1656.73 + 1026.8) kg/day
|  | : | 4345.7263 | kg/day
| BOD5 | : | (919.93 + 571.49+ 217.6) kg/day
|  | : | 1709.0272 | kg/day
| TP | : | (30.32 + 46.34 + 1.36) kg/day
|  | : | 78.024 | kg/day
| Org-N | : | (69.3 + 92.24 + 2.72) kg/day
|  | : | 164.2622 | kg/day
| NH3-N | : | (1.31 + 263.04 + 1.36) kg/day
|  | : | 265.7083 | kg/day
| TKN | : | (164.26 + 265.71) kg/day
|  | : | 429.9704 | kg/day

## Sheet1
WITHOUT RECYCLE FLOW (18 MLD IS DIRECTLY TAKEN TO SBR INLET FROM OUTLET OF INLET UNITS)
| Raw Sewage |  | Primary clarifier inlet | Bypass flow | Primary Sludge | Primary clarifier Effluent |  | SBR inlet |  | SBR
Flow (m3/d) | 100000 |  | 82000 | 18000 | 477.6699 | 81522.3301 |  | 99522.3301 |  | 99.522
Parameters | Mass (kg/d) | Con (mg/L) | Mass (kg/d) | Mass (kg/d) | Mass (kg/d) | Removal % | Mass (kg/d) | Mass (kg/d) | Con (mg/L)
TSS | 40000 | 400 | 32800 | 7200 | 19680 | 60 | 13120 | 20320 | 204.1753 | 205
BOD5 | 35000 | 350 | 28700 | 6300 | 10045 | 35 | 18655 | 24955 | 250.7477 | 250.8
TP | 700 | 7 | 574 | 126 | 57.4 | 10 | 516.6 | 642.6 | 6.4568 | 6.5
NH3-N | 5000 | 50 | 4100 | 900 | 0 | 0 | 4100 | 5000 | 50.24 | 50.3
Org-N | 1000 | 10 | 820 | 180 | 328 | 40 | 492 | 672 | 6.7523 | 6.75
TKN | 6000 | 60 | 4920 | 1080 | 328 |  | 4592 | 5672 | 56.9922 | 57
WITH RECYCLE FLOW (16.5 MLD IS DIRECTLY TAKEN TO SBR INLET FROM OUTLET OF INLET UNITS)
| Raw Sewage |  | Recycled Filtrate | Combined inlet to Plant |  | Primary clarifier inlet | Bypass flow | Primary Sludge | Primary clarifier Effluent |  | SBR inlet |  | SBR inlet parameters considered for design |  |  | COD/BOD | 1.86
Flow (m3/d) | 100000 |  | 4100 | 104100 |  | 87600 | 16500 | 543.4495 | 87056.5505 |  | 103556.5505 |  | 103600 |  |  | Inlet BOD | 352.6324 | mg/L
Parameters | Mass (kg/d) | Con (mg/L) | Mass (kg/d) | Mass (kg/d) | Con (mg/L) | Mass (kg/d) | Mass (kg/d) | Mass (kg/d) | Removal % | Mass (kg/d) | Mass (kg/d) | Con (mg/L) | Con (mg/L) |  |  | Inlet COD | 655.8962 | mg/L
TSS | 40000 | 400 | 4345.73 | 44345.73 | 425.9916 | 37316.8679 | 7028.8621 | 22390.1207 | 60 | 14926.7472 | 21955.6093 | 212.0156 | 212 | COD | 462.9097 | PST Bypass | 16.5 | MLD
BOD5 | 35000 | 350 | 1709.03 | 36709.03 | 352.6324 | 30890.5959 | 5818.4341 | 10811.7085 | 35 | 20078.8873 | 25897.3215 | 250.079 | 250 |  |  | COD in PST bypass | 10822.2875 | kg/day
TP | 700 | 7 | 78.02 | 778.02 | 7.4738 | 654.7027 | 123.3173 | 65.4703 | 10 | 589.2324 | 712.5497 | 6.8808 | 6.88 |  |  | COD in clarified | 37115.0402 | kg/day
NH3-N | 5000 | 50 | 265.71 | 5265.71 | 50.5832 | 4431.0874 | 834.6226 | 0 | 0 | 4431.0874 | 5265.71 | 50.8486 | 50.9 |  |  | COD in SBR inlet | 47937.3277 | kg/day
Org-N | 1000 | 10 | 164.26 | 1164.26 | 11.1841 | 979.7231 | 184.5369 | 391.8892 | 40 | 587.8339 | 772.3708 | 7.4584 | 7.5 |  |  | COD in SBR inlet | 462.9097 | mg/L
TKN | 6000 | 60 | 429.97 | 6429.97 | 61.7672 | 5410.8105 | 1019.1595 | 391.8892 |  | 5018.9212 | 6038.0808 | 58.3071 | 58.4

## Sheet2
Flow |  |  | = | 60 | MLD
Inlet TKN |  |  | = | 60 | mg/L | 3600 | kg/d
Inlet TP |  |  | = | 7 | mg/L | 420 | kg/d | Parameter | Raw water |  | Primary sludge |  | Primary outlet | BNR sludge | Combined sludge
Inlet BOD |  |  | = | 350 | mg/L | 21000 | kg/d | Flow (MLD) | 60 |  | 0.34951 |  | 59.6505 | 0.79963 | 1.0207
Inlet TSS |  |  | = | 400 | mg/L | 24000 | kg/d |  | Con (mg/L) | Mass (kg/d) | Removal % | Mass (kg/d) | Mass (kg/d) | Mass (kg/d) | Mass (kg/d)
Inlet ON |  |  | = | 10 | mg/L | 600 | kg/d | TSS | 400 | 24000 | 60 | 14400 | 9600 | 6525 | 20925
Inlet NH4-N |  |  | = | 50 | mg/L | 3000 | kg/d | BOD | 350 | 21000 | 35 | 7350 | 13650 | 4098.3285 | 11448.3285
[8 empty] | ON | 10 | 600 | 35 | 210 | 390 | 636.84 | 846.84
Sludge from primary |  |  | = | 14400 | kg/day |  |  | TKN | 60 | 3600 |  | 210 | 3390 | 636.84 | 846.84
|  |  | = | 349.5146 | m3/d |  |  | TP | 7 | 420 | 10 | 42 | 378 | 319.1491 | 361.1491
Sludge from Secondary |  |  | = | 6525 | kg/day |  |  | NH4-N | 50 | 3000 | 0 | 0 | 3000 | 0 | 0
|  |  | = | 799.6324 | m3/d |  |  | Nitrate N | [5 empty] | 6.3971
[8 empty] | TN | [5 empty] | 644.0367
Primary sludge
NH4-N removal is assumed to be zero
Assume 35 %ON removal
Inlet ON |  |  | = | 600 | kg/d
ON in sludge |  |  | = | 210 | kg/d
Assume 10%TP removal
Inlet TP |  |  | = | 420 | kg/d
TP in sludge |  |  | = | 42 | kg/d
Assume 35 % BOD removal
Inlet BOD |  |  | = | 21000 | kg/d
BOD in sludge |  |  | = | 7350 | kg/d
Assume 60 % TSS removal
Inlet TSS |  |  | = | 24000 | kg/d
TSS in sludge |  |  | = | 14400 | kg/d
Secondary sludge
NITROGEN IN BIOLOGICAL SLUDGE
Org-N in TSS |  | = | 0.122 kg org-N/kg TVSS x 0.8 kg TVSS/kg TSS
(Soluble org-N is neglected, since small quantity) |  | = | 636.84 | kg/day
NH4-N |  | = | 1 g /m3 of sludge
|  | = | 799.6324 | g/d
|  |  | 0.79963 | kg/day | NEGLIGIBLE
Nitrate -N |  | = | 8 g/ m3 of sludge
|  | = | 6397.0588 | g/d
|  | = | 6.3971 | kg/day
TN |  | = | 644.0367 | kg/day
BOD in the TSS from ASP |  | = | 0.65x1.42x0.68xTSS
|  |  | 4095.351 | kg/day
Soluble BOD5 in the effluent (S) |  | = | Total BOD5 in the Effluent - BOD5 exerted by TSS in the effluent
BOD5 exerted by TSS in effluent |  | = | (10 mg/L TSS) x (0.65 biodegradable solids/kg TSS) x (1.42 kg BODL/ kg biodegradable solids) x (0.68 kg BOD5 / kg BODL)
|  | = | 6.2764 | mg/L
| S | = | 10 mg/L-6.3 mg/L
|  |  | 3.7236 | mg/L
Soluble BOD in the sludge |  | = | 3.7 mg/L*Sludge flow
Sludge flow |  | = | 799.6324 | m3/d
Soluble BOD in the sludge |  | = | 2.9775 | kg/day
Total BOD in ASP sludge |  | = | 4098.3285 | kg/day
BOD5 in Sludge (including soluble BOD)
Inlet BOD5 |  |  | = | 13650 | kg/d
BOD5 in sludge |  |  | = | 4098.3285 | kg/d
SBR inlet TP |  |  | = | 378 | kg/d
Treated outlet flow |  |  | = | 58.8509 | MLD
TP in the outlet |  |  | = | 58.8509 | kg/d
TP in SBR sludge |  |  | = | 319.1491 | kg/d
TSS in sludge
Inlet TSS |  |  | = | 9600 | kg/d
TSS in sludge |  |  | = | 6525 | kg/d
|  |  |  | 799.6324 | m3/d