## hebbal
COMPLIANCE STATEMENT
Project |  | Design & Construction of 100 MLD STP at Hebbal with SBR and BNR, 10 years O&M
Client |  | Bangalore Water Supply and Sewerage Board
Consultant |  | NJS Engineers India Pvt. Ltd.
Document Title |  | Basic Engineering Package
Document No. |  | ECAIPL/BWSSB/STP/HEB/P/BEP-R0
BWSSB Letter No. |  | BWSSB/EE(STP)V&H/PB/825/2017-18 |  | Dtd. 09-11-2017
Sl.No | Comments |  | Document No. | ENVIRO Reply
ECAIPL/BWSSB/STP/HEB/P/BEP-R0
1 | Refer Chapter 1, page 7 of 56: The sludge in the thickener feed sump shall be mixed through either submersible mixer or through pump recirculation. Contractor mentioned that "The said scope of work is not mentioned in tender. It shall be treated as additional scope of work". |  |  | Noted.
Chapter 2, Mass balance calculation Excel sheet.
2 | Refer Cell J284: The thickened sludge consistency has been considered as 8%. Please confirm that it is achievable with the proposed screw thickener. |  |  | Confirmed.
Chapter 3, Process Design Calculaton Excel Sheet
3 | Refer Cell H73: Standard Engineering practice is to provide manual screens for 100% of the peak flow; however, as you intend to provide manual screens for 50% of the peak flow, please provide power back up to operate all the Mechanical Screens and associated conveyors during power faliure. |  |  | We shall consider manual screens for 50% of peak flow with provision of power backup to operate all the mechanical screens and associated conveyors during power failure.
4 | Refer Cell H706: The value of 22390 can be found in process design calculation, but not in Mass Balance. Please check and revise as necessary. |  |  | The value of primary sludge production as 22390 kg/day was found after the mass balance calculation, whereas, the value of 19680 kg/day shown in mass balance diagram is part of first iteration without recycle flow. The primary sludge produced before and after the mass balance has been included in the Table -1 & Table -2 of the Mass Balance diagram (R1).
5 | The appropriate equipment shall be selected to effectively mix the thickened sludge that will have solids content of 8%. |  |  | Confirmed.
Basic Engineering Package for CTEC SBR
6 | Refer Annexure IV, PDV of SBR, Page no. 3 of 53: The response to point no. 15 (Pl. refer Annexure-1) states recycle flow of 4.1 MLD, whereas the SBR documents states 3.6 MLD. Please revise SBR write up to be consistent. |  |  | The total flow to the inlet chamber of the STP shall be 104.1 MLD (= 100 MLD average flow + 4.1 MLD recycle flow) and to SBR shall be 103.6 MLD (= 104.1 MLD - Primary sludge removed). The document has been revised accordingly.
7 | Refer Page 6, Process Description: What is provided a standard DO control, and not 'automatic control of oxygen uptake rate.' Please delete this text from the BEP, and replace it with 'automatic dissolved oxygen control.' |  |  | Noted. The document has been revised accordingly.