## Sheet1
Contractor Letter Ref. No. |  | DATE
NJSEI Received |  | DATE
Project: Design & Construction of 100 MLD STP at Hebbal with SBR and BNR, 10 years O &M
Document Description: Basic Engineering Package
Sr. No. | Comments | Document No. | Status /Action
ECAIPL/BWSSB/STP/HEB/P/BEP
1 | The maximum TSS at the outlet of SBR is assumed as 15 mg/L. The contractor should use a value of 20 mg/L to determine the capacity of disc filtration system. | Chapter 1, page 5 of 49 | Confirmed. BEP has been revised and submitted accordingly.
2 | The sludge in the thickener feed sump shall be mixed through either submersible mixer or through pump recirculation. | Chapter 1, page 7 of 49 | The said scope of work is not mentioned in tender. It shall be treated as additional scope of work.
3 | The number of thickening polymer dosing pumps should be the same number of thickeners i.e. 2W+2S so that a dedicated dosing pump is provided for each thickener. | Chapter 1, page 7 of 49 | Confirmed.BEP has been revised and submitted accordingly.
4 | The sludge from existing 60 MLD STP is proposed to be received in the thickened sludge sump. Please confirm that the gravity sludge thickener is the existing STP is in good working condition, and it will thicken the sludge and only the thickened sludge will be pumped to the proposed sludge handling plant. | Chapter 1, page 7 of 49 | Kindly refer scope of work mentioned in Volume II, Section 7, Part-1, Page 1-3, 6th para. As per discussion held with M/S. NJS and CE BWSSB, the existing thickeners are not in good working condition and hence, it was decided to adopt 1 No. of mechanical screw thickeners out of 2 Nos. of standby thickeners proposed for new 100 MLD STP at Hebbal which is highly appreciated to achieve better sludge quality. Moreover, 1 No. of poly dosing pump shall also be provided from proposed STP to BWSSB for their future utilization of the screw thickener.
5 | One (1) heat exchanger has been proposed to increase the sludge temperature to achieve digester temperature of 30oC. Please confirm that one heat exchanger per digester (total of 4 Nos.) will be provided with appropriate interconnecting pipework to maintain digester temperature during heat exchanger maintenance. | Chapter 1, page 7 of 49 | Kindly refer Clause No. 11, corrigendum-I dtd: 6-05-17. "Bidder may propose heat exchanger system to maintain required temperature inside sludge digester to achieve guaranteed power generation through biogas engine". To achieve guaranteed power generation, i.e. 6384 kWh/day through biogas engine, we require only 413 m3/hr (max.) quantity of biogas generated from anaerobic digester. To achieve the said quantity and guaranteed power generation, the heat exchanger is not required as per the above said corrigendum-I, which supersedes tender specifications and therefore, we had offered discount of Rs. 1,56,64,231.00 in price schedule-III, c.3.2.5.3, digester gas mixing blower, sludge mixing pumps, scrubbers, heaters, SS316 piping, vide our letter no. ECAIPL/BWSSB/STP-H/05/17-18 dated July 6th, 2017 after opening of price bid on special request from the then CE, BWSSB and Chairman, BWSSB.
Technical Justification With the process fundamentals and available international references, we observe that volatile solids destruction can be achieved about 55% at 24oC temperature with SRT of 8-20 days. However, we have provided digestion time of 23.5 days for wastewater of temperature 26-29oC as per tender, Vol -II, Part 5, Section 7, Pg. 5-23. Moreover, for design purpose we have assumed 52% of VSS destruction in high rate complete mix anaerobic digestion process. Hence, average biogas yield of 0.9 m3/kg of VSS destructed shall generate 757.71 m3/hr of biogas. The required biogas quantity is only 413 m3/hr to produce guaranteed power generation of 6384 kWh/day and remaining additional quantity shall be stored in biogas holder and hence, heat exchanger is neither required nor it is mandatory as per corrigendum-I dtd: 6-05-17.
Guaranteed power generation = 6384 units/day Required biogas quantity = 395 m3/hr (min.) to 413 m3/hr (max) Design temperature = 24oC VSS destructed = 52% Biogas yield = 0.9 m3/kg of VSS destructed kg VSS destructed = 0.52 x 38797.18 kg/day = 20205.57 kg/day Biogas production = 757.71 m3/hr Required biogas quantity = 413 m3/hr (max.). Hence O.K.
Necessary relevent documents are enclosed herewith. (a) Load calculation from Gas engine vendor. (b) Calculation of guaranteed power generation in terms of kwh/day based on submitted technical bid during tender stage. Kindly refer the following references for the above technical justification. - Van Haandel, A., & Van Der Lubbe, J. (2012). Handbook of Biological Wastewater Treatment: Design and Optimisation of Activated Sludge Sysyems. 2nd Edition.Chapter 12, Figure: 12.9, Pg. 440, IWA Publishing. (Ref.4) - Manual on Sewerage and Sewage Treatment Systems. (2013). CPHEEO. Part A: Engineering, Chapter 6,Table: 6.9, Figure: 6.7, Pg.:6-33. (Ref.3) - WEF Manual of Practice No.8 ASCE Manuals and reports on Engineering practice No. 76, Design of Municipal Wastewater treatment Plants, (2009). 5th Edition, Volume 3, Chapter 25, Cl. 2.2.5, Fig. 25.2, Pg. 25-21, McGraw Hill. (Ref.5) - Metcalf and Eddy.( 2014). Wastewater Engineering Treatment and Resource Recovery, 5th Edition,Chapter 13, Table 13-27, Pg. : 1507, McGraw Hill Education (Ref.6) - Metcalf and Eddy. (2014). Wastewater Engineering Treatment and Resource Recovery, 5th Edition, Chapter 13, Table 13-30, Pg. : 1510, McGraw Hill Education (Ref.8)
6 | Please clarify whether the waste heat recovery system will be provided along with the biogas engines. | Chapter 1, page 7 of 49 | The waste heat recovery system will not be provided as it is not required as per reply no. 5.
7 | Clarify how the design digester temperature of 300C will be achieved during initial commissioning and during the period when the biogas engine will be under annual maintenance or out of service. | Chapter 1, page 7 of 49 | Please refer reply of Point 5 regarding the same.
8 | Clarify the flow splitting mechanism to achieve the target BOD of 250 mg/L at the SBR inlet. This mechanism should comply with requirement specified in Part 5, Section 5.1 | Chapter 1, Page 9 of 49 | Kindly refer note mentioned in Vol-II, sect-7, part-II. "Tenderer to propose all the units/equipments as per his own layout and designs for successful commissioning & operation of the project".The plant is designed to achieve guaranteed effluent quality based on BNR process.
9 | Clarify the flow splitting strategy and its impact on the downstream units when the influent BOD is less than 250 mg/L | Chapter 1, Page 9 of 49 | Please refer the description (step -I & II), Page 9 of 56 of BEP (ECAIPL/BWSSB/STP/HEB/P/BEP-R0). A PST bypass sewage stream shall be provided from the common outlet channel of vortex grit chamber, which is to be blended with settled sewage at the splitter box to achieve BOD5 at the SBR inlet as 250 mg/L for efficient BNR process to get desired outlet discharge norms for TN and TP as per tender. Hence, two different parshall flumes shall be provided to serve the purpose with flow measuring and regulating units. The Parshall flume -I shall be provided for stream having PST followed by SBR, whereas Parshall flume - II shall be provided for raw sewage after degritting conveying directly to SBR.
The Parshall flume - II should carry an average flow of 18 MLD (initially) when there is no recycle flow, whereas, after mass balance, the flow required is 16.5 MLD for the said stream. Hence, the Parshall flume- I shall be designed for peak flow of 171.1 MLD [=(204.1-(16.5*2)) MLD] and the required design flow for Parshall flume-II shall be 18 MLD (initial flow) x 2.0 PF = 36 MLD. However, we agreed to design Parshall flume - II considering 50 MLD as per your comment given in point no:23. The isolation gate and weir arrangement shall be provided accordingly and shown the same in HDF calculation, which will be submitted separately.
Chapter 2, Mass balance calculation Excel sheet
10 | In the Mass Balance calculation, the combined sludge consistency is assumed to be 2 %, whereas based on the provided sludge quantities and consistencies for primary sludge and WAS, the calculated value comes to 1.54 %, which will increase the thickener feed flow to 2096.6 m3/day. Please revise accordingly. | Cell J79 | Noted. BEP has been revised and submitted accordingly.
11 | Please calculate the combined sludge consistency for the exisiting 60 MLD STP. | Cell J245 | Noted. BEP has been revised and submitted accordingly.
12 | The sludge consistency to anaerobic digester is assumed at 4.5 %. Please calculate the value using the thickened sludge solids and consistency. | Cell J297 | Noted. BEP has been revised and submitted accordingly.
14 | Thickening polymer and dewatering polymer dose rates are assumed as 2 kg/MT and 4kg/MT. The dewatering polymer dose appears to be low for producing cake solids of 6 - 8 kg/MT may be considered. | Cell J361 | As per manufacturer , 4 kg/MT dosing rate is required to achieve 25 % consistency. However, considering safety factor of 1.5 as per tender, the dosing shall be considered as 1.5*4 = 6 kg/MT to find out the storage volume of the poly dosing tank and pumps for COTDM unit.
15 | The combined recycled flow of 3894 m3/day shall be rounded to 4000 m3/day and not 3500 m3/day. | Cell J468 | Noted. Revised value of recycle flow is 4032.95 m3/day. However, the quantity of recycled flow is considered as 4100 m3/day for design purpose.
Chapter 3, Process Design Calculation Excell Sheet
16 | Total manual screens are 2 nos, so the flow per screen should be 2.89 m3/sec. Please rectify | Cell H73 | Tender does not specify to provide 100 % stand by capacity of manual screen. Hence, 50 % of capacity of screen has been considered as per standard engineering practice and followed the pattern of standby unit provision mentioned in the tender for all mechanical equipments. The quantity of total design flow for two standby screens has been changed in the revised BEP.
17 | As per Section 5.1 of Part 5, the design peak flow should be 250 MLD for inlet units of the STP (inlet channel, fine screens, grit chamber), whereas peak flow considered for these units is 200 MLD. Please verify and revise the sizing of these units accordingly. | Cell E142. Please refer sec-7, clause 5.13.1, part-5, page 5-23. | Please refer Volume 2, Section -7, Clause 5.13.1, Part 5, pg. 5-23. The design peak flow shall be 200 MLD for inlet units of the STP + other flow. Moreover, the screen doccuments received from BWSSB mentioned the flow per screen for 2 Nos. working as 112.32 MLD and the flow per standby screen (1 No.) as 120 MLD. i.e., screen channel has to be designed for total design flow of 112.32 x 2 = 224.64 MLD, say 225 MLD instead of 250 MLD as peak flow. Therefore, we suggest to adopt 225 MLD instead of 250 MLD. Therefore, we suggest to adopt 225 MLD instead of 250 MLD as design flow for inlet chamber, Screen channel and grit chambers. We have designed the said units accordingly.
18 | The other flow (recycle flow) should be considered as 4 MLD as per comment 15 above. | Cell E143 | Please refer reply against point no. 15.
19 | Please provide the fine screen literature to support the fine screen channel sizing. | Row 186 | It shall be provided by BWSSB as it is not in our scope of work. Moreover, BWSSB has to confirm that size of mechanical screens are sufficient to handle total design flow of 225 MLD as per above point no. 17.
20 | The sizing of structures such as screen channels, grit chambers should be based on the equipment available in the market. If any changes are required to these structures after approval of the equipment data sheet, the same shall be incorporated. |  | Noted. Confirmed.
21 | In view of the comment no 9 above, it is suggested that the Parshall Flume-I and the downstream structures such as Primary clarifier distribution chamber, primary clarifier etc. shall be designed to accept full plant flow, i.e. the peak flow of 203.5 (204) MLD. | Row 268 | Please refer reply given against your point no.9. Hence, stream including PF-I followed by PST etc. shall be designed for 171.1 MLD to achieve efficient BNR process. Please also refer the revised BEP for further explanation/details regarding your query.
22 | The dimensions of the Primary Clarifier Distribution Chamber are not complying with those given in Part 5 (page 5-27) Employer's requirement. Please revise. | Cells H311, H313, H315 | Please refer note mentioned in Volume II, Part-11, Sect-7. As per own design of EPC contractor, the size of PST distribution chamber is calculated considering minimum 15 sec of HRT to achieve better hydraulic flow condition.
23 | As the calculated SOR for primary clarifier is less than 35 m3/m2/d (about 32 m3/m2/d for the design diameter of 29.5 m), it is suggested that the Parshall Flume - II (bypass to SBR) be designed for 50 MLD (25 % of the flow) so that sufficient BOD can be provided to SBR in case of excessive removal in the primary clarifier occurs during operation. | Cell H341 | Confirmed. BEP has been revised and submitted accordingly.
24 | As per comment no 1 above, assume the maximum TSS at SBR outlet of 20 mg/L. | Cell H525 | SBR is designed to achieve outlet TSS as 10 mg/L. However, for design of disc filter, we shall consider TSS at SBR outlet as 20 mg/L.
25 | The detention time for Treated Sewage Outlet chamber is considered as 10 seconds, whereas detention time for all such other chambers is 15 seconds. Hence revise the detention time to 15 seconds. | Cell H534 | Confirmed. BEP has been revised and submitted accordingly.
26 | The volume of the plant drain sump is calculated using only the primary clarifier drain volume. Please clarify how the regular drains such as filter backwash, dewatering centrate, thickening filtrate etc. will be recycled back. If all these flows are to be recycled back through the plant drain sump, please provide a total flow balance for the sump and then calculate the sump volume using detention time of 10 minutes. | Cell H556 | The filtrate sump with pump facility is provided as per tender to recycle back the regular drains such as filter backwash, dewatering centrate, thickening filtrate etc to inlet of STP. Hence, plant drain sump design is O.K. Please refer corrigendum-I dated 06-05-17, point no. 9 and Volume-II, Part 11, item No. 27.
27 | The primary sludge quantity in the process design calculations is 21844 kg/d, whereas its quantity in the Mass Balance is 19680 kg/d. Please resolve the descripancy so that both documents have the same value. Please appropriatley link both these documents for a consistent design documentation. | Cell H610 (and cell J24 in Mass Balance sheet) | Kindly refer the note mentioned in the design basis in Clause 3.3, chapter 3, page 38 of 56 of BEP ECAIPL/BWSSB/STP/HEB/P/BEP-R0. The sludge handling units are designed for the required quantity of sludge production, obtained after the Mass Balance Calculation. The primary sludge production (revised) obtained after the mass balance calculation is 0.6*425.99 mg/L* 87.6 MLD = 22390.03 kg/day (Refer Table 2: Column 6, Row 5 & Column 7, Row 3 in Mass balance diagram in Annexure : I)
28 | The calculated thickener feed flow is 36.22 m3/hr (cell H668), however the provided pump and thickener are of capacity 55 m3/hr as required by the contract. This will result in thickener operation of only 16 hrs against the assumed continuous operation. Therefore, provide variable speed drivers for the thickener feed pumps to operate those pumps at the required flow rate or provide sufficient storage on either side of the thickener (feed and discharge) so that the upstream and downstream units can be operated continuously / as designed. |  | As per revised BEP, the operational hours of thickener feed pump shall be 22 hrs considering 4 Nos. (2W+2S) of thickeners and hence, VFD is not required. The volume of sludge sump has been revised accordingly.
29 | Air blower are provided to mix the content of the thickened sludge tank. It is suggested to provide submersible mixer or pumped hydraulic mixing to avoid aeration of the sludge that will be fed to anaerobic digesters. This aeration can degrade the BOD in the primary sludge thereby reducing the biogas generation in the digesters. |  | Noted. However, Submersible mixers shall be additional scope of work as per tender.
30 | The digester feed pump operational hours are considered as 24 hours, which is okay for constant level digesters. If the digesters are going to be operated as variable level, i.e. filling, reacting, and wasting, then the feed pump operational hours could be less than 24. Please clarify the digester operation philosophy and then size the feed pumps accordingly. |  | Digester feed pumps shall be designed for 22 hrs of operation instead of 24 hrs. considered earlier. Hence, the design of sludge sump and pumps has been revised accordingly. As referred, the level of digester shall be maintained at constant desired level and therefore, the variable sludge level will not be applicable in digester operational philosophy. The differential pressure type of level instrument may be installed on digesters to maintain constant high sludge level in the digester. This instrument will measure the pressure at high pressure end (bottom of digester) and low pressure end (top of digester) through capillary filled tubes. The difference of pressure shall be calibrated in terms of the sludge level and shall be communicated to PLC as level in terms of 4-20 mA. Accordingly, the PLC shall operate the digester feed pumps to maintain the desired constant level by making the feed pump ON/OFF. The schematic sketch of above arrangements of the level measuring instrument is shown in Annexure V. Moreover, fill and spill arrangement with bell mouth shall also be provided to maintain the required TWL in the anaerobic digester. The details of this arrangement shall be shown in the G.A. drawing of the Anaerobic sludge digester.
31 | For anaerobic digesters, the bottom cone slope should be 1:3, and allowance of 0.5 m shall be provided for foam and scum accumulation (as per Part 5, page 5-30). The free board of 1 m is acceptable. Therefore, the digester depth (excluding hopper) would be 11 m against 10.5 m. | Cell H754 | As tender does not specify allowance of 0.5 m additional depth to be provided as part of SWD and, it is also not mandatory as per process requirement. Hence, we shall provide 1.65 m average depth of allowance in hopper bottom of digester which is more than sufficient to fullfill the requirement of tender without any deviation from tender clause.
32 | The conduction heat loss from digester is assumed to be 20% of heat required to heat the raw sludge. However, our rough calculations show that the conduction heat loss from digesters can be almost 100% during winter months. So please provide back-up calculations for the assumed conduction heat loss. | Row 807 | To achieve guaranteed power generation, the heat exchanger is not required (please refer reply against your comment no.5).
33 | The capacity of the biogas engine feed blower is considered as 500m3/hr. However, if the feed rate for the engine as per the Engine datasheet is more, then the blower of corresponding (higher) capacity shall be provided. | Cell H865 | Noted. 500 m3/hr capacity is sufficient as per manufacturer. Hence, it is O.K.
34 | The retention time for the Digested Sludge / COTDM Feed Sump is considered to be 1 hour. This appears to be low, and its correctness can be evaluated only after understanding the digester operation philosophy (feeding and wasting pattern). So the sump retention time is put on hold till, and subject to revision after review of digester operation philosophy. | Cell H887 | The digester shall be operated at constant water level to maintain designed TWL and liquid volume by providing arrangement mentioned in reply no. 30 and hence, 1 hr of HRT for digested sludge/ COTDM feed sump is sufficient.
35 | As per above comment no 15, consider total filtrate flow to be 4000 m3/d | Cell H942, H960 | Please refer reply against point no. 15.
36 | The runtime of thickened sludge transfer pumps is considered to be 24 hrs. Please review the operation of the thickening units in the existing 60 MLD plant and revise the pump runtime if necessary. | Cell H974 | With the proposed 55 m3/hr capacity screw thickener (as per reply to the comment no.4) to be adopted for existing STP, the operation time considered is 22 hrs. Hence, the pump run time is also considered as 22 hrs.
37 | The same polymer has been considered for thickening and dewatering. Please confirm that the same polymer is suitable for these operations | Cell H1090 | As per the manufacturer, same type of polymer is suitable for thickening and dewatering. Hence, O.K.
38 | Regarding polymer bag storage area, 63 bags will be required, and a stack of 6 bags is proposed, thereby resulting in 11 stacks. However, only 6 stacks are considered in area calculation. Please rectify. | Cell H1103, H1104 | Noted. BEP has been revised and submitted accordingly.
39 | The COTDM polymer dosing pump capacity is calculated based on total polymer quantity required. Please calculate the dosing pump capacity based on the COTDM machine capacity, and check whether the provided capacity is adequate to operate the machine at rated flow. If not, then the dosing pump capacity shall be revised. | Cell H1136 | Noted. The capacity of COTDM polymer dosing pump has been revised accordingly.
40 | The number of screw thickeners are 4 Nos. Hence the number of polymer dosing pumps should be at least 4 nos. Please rectify. | Cell H1142 | Noted. Confirmed
41 | The thickening polymer dosing pump capacity is calculated based on total polymer quantity required. Please calculate the dosing pump capacity based on the screw thickener machine capacity, and check whether the provided capacity is adequate to operate the machine at rated flow. If not, then the dosing pump capacity shall be revised. | Cell H1146 | Noted. The capacity of thickener polymer dosing pump has been revised accordingly.
42 | The polymer and alum dosing tanks filling time assumed are too long (12 hrs and 16 hrs). These should be less than 2 hours each. Please revise as necessary. | Cell H1233 and H1236 | Confirmed. BEP has been revised and submitted accordingly.
43 | The number of process units mentioned on the Process Flow Diagram should match with the number of units in Process Design Calculation | Process Flow Diagram | Noted. Confirmed.
44 | The sludge generation calculation accounts only for heterotrophic biomasss yield and inert TSS. The sludge generation due to cell debris and non-biodegradable VSS has not been calculated. Please revised the sludge production (refer equation 7-56 in Wastewater Design by Metcalf & Eddy); the observed sludge yield would be almost 0.7 kg/kg-BOD against the calculated yield of 0.549 kg/kg-BOD. The CPHEEO Manual also provides a range of 0.75 – 1.0 for Sludge Yield in SBR (CPHEEO, Page 5-198). So accordingly revise the process design calculations for the sludge handling. | Sludge Generation Calculation (Excel sheet) | Kindly refer Clause No. 11, corrigendum-III dtd: 16-05-17 "13." SBR system including decanter, air &diffuser system and process design can be provided as per standard design of technology provider or as per latest CPHEEO manual." The Sludge calculation has been revised as per Metcalf and Eddy. Moreover, the range of 0.75 – 1.0 mentioned in the CPHEEO manual is for unsettled sewage (Ref.13), which is not applicable for the proposed STP where the SBR feed is from the Primary clarifier and hence the sludge generation is much lower.
Basic Engineering Package for CTEC SBR
45 | In Design Basis, the Daily Other Flow should be considered as 4 MLD instead of 3 MLD | Page 3, Design Basis | Please refer reply against point no. 15.
46 | In Outlet Parameters, Sl. No. 8 should be Total Nitrogen (as N) | Page 4, Outlet Parameters | Noted. BEP has been revised and submitted accordingly.
47 | Process description states ‘automatic control of oxygen uptake rate’. Please provide appropriate instrumentation and logic to achieve this. | Page 6, Process Description | The control is achieved through DO measurement and control of blower speed through VFD in order to achieve the DO set point. Each basin is equipped with DO transmitter and the blowers provided are capable of variable speed operation. Hence adequate instrumentation and control is provided.
48 | In Design Basis adopted for SBR calculations, please rectify the outlet Nitrate N as < 7mg/l | Page 18 | Noted.
49 | Please revise the Excess Sludge quantity on Page 19 in view of the comment no. 44 above. | Page 19 | Please refer reply against your comment No. 44.
50 | Please revise the calculated SRT in view of the comment no 44 above. This revised SRT should be more than 12 days to provide 6 days of aerobic SRT as discussed during various meetings. | Page 26 | Noted.
51 | The anaerobic SRT calculation should be revised in view of comment no 50, and considering the anaerobic fraction as 0.25 (6 hr/d) and not 0.3. | Page 26 | It is appearing as 0.3 as an approximation in Excel, while it is actually = 3706.5/13900 = 0.266
52 | On page 11, the Selector contact time of 60 minutes is nominated as Design Value, whereas on page 28 the Selector contact time provided is 35 minutes. Please clarify. | Page 11 and Page 28 | As per Metcalf and Eddy page number 701 contact time for selector is 20 to 60 min. Hence, for design contact time of 35 min has been considered.
53 | Oxygen calculations are not as per the conditions stipulated in the Contract in Part 5, Page 5-15. If those conditions are followed, the oxygen requirement comes to 48218 kg/d. Even if the oxygen requirement of 1.1 kgO2/kgBOD is used, the total oxygen requirement comes to 45746 kg/d. Whereas the oxygen requirement in process calculations is 39373 kg/d, which is much lower. Please rectify, and then accordingly revise the air requirement calculations and blower capacity. | Page 36 – 40. | Kindly refer Clause No. 11, corrigendum-III dtd: 16-05-17 "13." SBR system including decanter, air &diffuser system and process design can be provided as per standard design of technology provider or as per latest CPHEEO manual."This supersedes tender specifications which forms part of this tender , wherever applicable. We have verified air calculations and found OK. Following standards have been considered for air requirement calculations, 1)Air requirement for BOD removal = 1.1 kg of O2 / kg of BOD removal (As per CPHEEO manual 2013, page no 5-198). 2)BOD requirement per g of Nitrate reduction (denitrification) - As per Metcalf and Eddy page no 620. We wish to highlight here that the same format of air calculations has been approved by BWSSB in the earlier package "S1a1 STP" JICA tenders.
54 | Sludge generation calculations are to be revised in view of comment no 44 | Page 40 | Please refer reply against your comment No. 44
55 | The air requirement when 1 basin is offline is to be revised in view of comment no 53 above. | Page 45 | Please refer reply against your comment No. 53